## Sheet1
RWI System - Active elements	FUNC	Denomination	Manufacturer	Location

P1 - sumergible pump 220VAC/0.75kW, 1”, 80m,	ON/OFF initiated by “High Tank” Low Level Threshold or pressure compensation request initiated by PRS2 for pressurized system; / Where PRS2 has first priority and HighTank second, PRS2 request will interrupt HighTank / Sequence, if active, serve PRS2 request until / Necessary, wait 5min before continue se interrupted HigTankrequestON/OFF initiated by High/Low Level threshold from HighTank LVS2, or PRS2 High/Low Level threshold, Valves V1/V2 must be switch acordingly	HT_HLT / HT_LLT / PRS2_HLT / PRS2_LLT			P1 is submergable with 80m capacity
powered with SSR08x3,		SSR08x3 / Channel 1			3-Channel SSR 220VAC@4A continue
controlled by BASST,		BASST			MCU / WiFi / ESP32 Base Station Controller

P2 - filter reverse wash	not used yet

P3 - Feed Pump, sumergible,	ON/OFF initiated by LVS1 Low Level threshold “Low Tank” o TB2-ManualSwitch override				P3 is a submergable pump 24VDC 1100 liter/h / To feed water from the Open-air Tank to the Low Tank
+24V@5A,				TB2	Power Supply 24VDC@5A, feeding P3 and REMST

SSR-DC-24V@5A	ON/OFF initiated by water transfer request from LVS1 Low Level threshold,	SSR08x10_DC		TB2
controlled by REMST_00
FUNC :
- TB2 manual operation	manual override
- ON/OFF // PWM	automatic control by system

RWI - System Board,		RWI_00		TB1	MCU peripheric interface / PWS for UK2.4N connector
System PWS, +24V, +5V, +3V3, +Loop, +5V-S,		RWI_00

Field Connector		28-PIN UK2.5N
.Module_BASST_00,		BASST_00
.Module_DCIN_00,		DCIN_00
.Module_DCOUT_00,		DCOUT_00,
.Module_SSR08x4,		SSR08x
>> DC Input Module 3V3 / 5V -
DCIN_00:		DCIN_00
PRS1 - pressure sensor #1 /	0.5...4.5V, pressure signal of stand-pipe, P1 control/protection	PRS1_30psi
Stand-Pipe pressure
30PSI / 0.5..4.5V
FUNC :
Normal Pump Active Value,
Low Threshold <= P1 ON
High Threshold >= P1 OFF
# monitores pump activity
# protects pump run-dry
# activates pump in pressurized
systems,

PRS2 - pressure sensor #2
- Pressurized System Controller
- 30PSI / 0.2....2.8V
FUNC :
- monitor pressurized system,
- maintain pressure,
- EV2/EV1,
- Activate/Desactivaste P1;
LVS1 - Level sensor
- +Loop Power
- 0...2m / 4..20mA
FUNC :
- Low Level Threshold
- High Level Threshold
- P3 control
- EV3 control
LVS2 - not used

>> Digital Inputs 3..12VDC@3mA

FLWS1 - Flow sensor
- Stand-Pipe
- 38 pulse / litro / +5V
FUNC :
- monitor P1 function
- protect P1 dry run

FLWS2 - Flow sensor
- Low Tank fill control;
- 38 pulse / litro
- Filter alarm
FUNC :
- monitor P3 function
- monitor Low Tank filling

DAUX1 - input not used
DAUX2 - input not used

>> Digital Outputs 24VDC/0.5A
DCOUT_00:
- EV1....5 - 5-Ch-SINK//PWM
O. C. 30V@0.5A;
FUNC :
- EV1 - fill High Tank
- EV2 - Pressurized Section
- EV3 - fill Low Tank
- EV4 - (filter revers wash)
- EV5 - (filter reverse wash)

SSR_Out - 4-Channel Sink SSR
- 220VAC / 4A SSR
FUNC :
CH1 - P1 ON/OFF
CH2 - (P2)
CH3 - not used
CH4 - not used

::::::: updated ::::::::::::::: 241024FB
REMST_00 Notes :
make Sensor Power controlable by program;